{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":8,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","3MXS-K"]
[]
[]
[]
[]
["","","","","","3MXS40K3V1B","3MXS40K3V1B2","3MXS40K2V1B"]
["Nivo zvučnog pritiska","Grejanje","","Nom.","dBA","47","47"]
["","Hlađenje","","Nom.","dBA","46","46"]
["Standardni pribor","Priručnik za instalaciju","","","","1","1"]
["","čep ispusnog otvora","","","","1","1"]
["Rashladno sredstvo","Charge","","","TCO2Eq","4.2","4.2"]
["","GWP (potencijal globalnog otopljavanja)","","","","2,087.5","2,087.5"]
["","Punjenje","","","kg","2.0","2.0"]
["","Tip","","","","R-410A","R-410A"]
["Cevne spojnice","Razlika nivoa","IU - IU","Maks.","m","7.5","7.5"]
["","","IU - OU","Maks.","m","15","15"]
["","Dodatna punjenje rashladnog sredstva","","","kg/m","0,02 (za dužinu cevovoda preko 30m)","0,02 (za dužinu cevovoda preko 30m)"]
["","Ukupna duћina cevi","Sistem","Aktuelno","m","50","50"]
["Kompresor","Tip","","","","Hermetički zatvoren klatni kompresor","Hermetički zatvoren klatni kompresor"]
["Dimenzije","Uređaj","","Širina","mm","936","936"]
["","","","Dubina","mm","300","300"]
["","","","Visina","mm","735","735"]
["Težina","Uređaj","","","kg","49","49"]
["Power supply","Faza","","","","1~","1~"]
["","Frekvencija","","","Hz","50","50"]
["","Napon","","","V","230","230"]
["Beleške","","","","","(1) - Sadrži fluorisane gasove sa efektom staklene bašte","(1) - Sadrži fluorisane gasove sa efektom staklene bašte"]
["Dimenzije","Uređaj","","Visina","mm","","","735"]
["","","","Širina","mm","","","936"]
["","","","Dimenzije-=-Uređaj-=-Dubina-=-mm","mm","","","300"]
["Težina","Uređaj","","","kg","","","49"]
["Kompresor","Tip","","","","","","Hermetički zatvoren klatni kompresor"]
["Radni opseg","Hlađenje","Spolja","Min.","°CDB","","","-10"]
["","","","Maks.","°CDB","","","46"]
["","Grejanje","Spolja","Min.","°CWB","","","-15"]
["","","","Maks.","°CWB","","","15.5"]
["Nivo zvučnog pritiska","Hlađenje","","Nom.","dBA","","","46"]
["","Grejanje","","Nom.","dBA","","","47"]
["Rashladni fluid","Tip","","","","","","R-410A"]
["","Količina","","","kg","","","2.0"]
["","Količina","","","tCO2Eq","","","4.2"]
["","GWP (potencijal globalnog otopljavanja)","","","","","","2087.5"]
["Cevne spojnice","Dužina cevovoda","Maks.","OU - IU","m","","","50"]
["","Dodatna punjenje rashladnog sredstva","","","kg/m","","","0,02 (za dužinu cevovoda preko 30m)"]
["","Razlika nivoa","IU - OU","Maks.","m","","","15"]
["","","IU - IU","Maks.","m","","","7.5"]
["Standardni pribor","Installation manual","","","","","","1"]
["","Drain plug","","","","","","1"]
["Napajanje","Faza","","","","","","1~"]
["Izvor napajanja","Frekvencija","","","Hz","","","50"]
["","Napon","","","V","","","230"]