{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":12,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZXRC2"]
[]
[]
[]
[]
["","","","","","EWADH12TZXRC2","EWADC15TZXRC2","EWADH16TZXRC2","EWADC12TZXRC2","EWADC11TZXRC2","EWADH17TZXRC2","EWADC14TZXRC2"]
["Kapacitet hlađenja","Nom.","","","kW","1,279","1,499","1,625","1,204","1,122","1,735","1,362"]
["Regulacija kapaciteta","Metod","","","","Varijabilna","Varijabilna","Varijabilna","Varijabilna","Varijabilna","Varijabilna","Varijabilna"]
["","Minimalni kapacitet","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Apsorbovana snaga","Hlađenje","","Nom.","kW","403","501.4","547.6","377.3","356.3","598.6","450.1"]
["EER","","","","","3.17","2.99","2.97","3.19","3.15","2.90","3.03"]
["IPLV","","","","","5.49","5.65","5.64","5.55","5.51","5.6","5.64"]
["SEER","","","","","5.32","5.31","5.31","5.33","5.30","5.32","5.27"]
["Dimenzije","Uređaj","","Dubina","mm","12,302","12,302","13,202","11,402","10,510","14,104","11,402"]
["","","","Visina","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Širina","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Težina","Radna težina","","","kg","11,526","12,145","12,575","11,123","9,879","13,048","11,727"]
["","Uređaj","","","kg","10,515","11,134","11,564","10,112","9,322","12,037","10,716"]
["Kućište","Boja","","","","Boja slonovače","Boja slonovače","Boja slonovače","Boja slonovače","Boja slonovače","Boja slonovače","Boja slonovače"]
["","Materijal","","","","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča","Galvanizovana i obojena čelična ploča"]
["Izmenjivač toplote vazduha","Tip","","","","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal"]
["Ventilator","Količina","","","","26","26","28","24","22","30","24"]
["","Tip","","","","Direktni pogon sa elisom","Direktni pogon sa elisom","Direktni pogon sa elisom","Direktni pogon sa elisom","Direktni pogon sa elisom","Direktni pogon sa elisom","Direktni pogon sa elisom"]
["Motor ventilatora","Pogon","","","","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)"]
["Kompresor","Količina_","","","","2","2","2","2","2","2","2"]
["","Tip","","","","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor","Kontinualni inverterski jednovijčani kompresor"]
["","Način pokretanja_","","","","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)","Na bazi VFD-a (promenljive brzine)"]
["Sound power level","Hlađenje","","Nom.","dBA","94","94","95","93","92","95","93"]
["Nivo zvučnog pritiska","Hlađenje","","Nom.","dBA","71","71","71","70","70","72","71"]
["Rashladno sredstvo","Tip","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","GWP (potencijal globalnog otopljavanja)","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Punjenje","","","kg","220","220","250","200","175","270","200"]
["","Kola","","Količina","","2","2","2","2","2","2","2"]
["Cevne spojnice","Ulaz/izlaz vode iz isparivača (sp.preč.)","","","","219.1","273","273","273","219.1","273","273"]
["Power supply","Faza","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Frekvencija","","","Hz","50","50","50","50","50","50","50"]
["","Napon","","","V","400","400","400","400","400","400","400"]
["","Naponski opseg","","Min.","%","-1","-1","-1","-1","-1","-1","-1"]
["","","","Maks.","%","-1","-1","-1","-1","-1","-1","-1"]
["Uređaj","Napon pokretanja","","Maks.","A","0.0","0.0","0.0","0.0","0.0","0.0","0.0"]
["","Radni napon","Hlađenje","Nom.","A","689.6","834.0","901.3","651.0","612.3","982.6","762.5"]
["","","","Maks.","A","994","1,124","1,218","939","918","1,313","1,085"]
["","Maksimalna struja za određivanje veličine kablova","","","A","1,093","1,236","1,340","1,033","1,010","1,444","1,194"]